## Slide 1: Barreleye G2 2.0 OU system Thermal Simulation Report rev. R10
Honda Yan
20170410

## Slide 2
Component | TDP (watts) | Q’ty. | Note
Power CPU | 225 | 2 | Spec, Tj, 85C
Memory | 5 | 32 | Spec, Tc, 85C
NVMe HDD | 9.0 6.3 | 8 16 | Spec, NAND : Tj, 85C Memory : Tj, 100C Controller : Tj, 125C
K80 | 300 | 2 | Spec, 14.5 CFM
VTM | 66 | 2 | Spec, Tc, 110C
6056 Fan |  | 6 | 
Power Brick | 18.11 | 1 | Flotherm Model provided from vendor
System configuration

## Slide 3
System placement
Nvidia K80 *2
CPU1
CPU2
Fan1
2.5” HDD Drawer
DIMM x32
VTM
VTM
Expender Board
Air flow direction
Fan2
Fan3
Fan4
Power Brick
Fan5
Fan6

## Slide 4
System Inlet / Outlet venting
Front view
Venting (open ratio=60%)
Rear view

## Slide 5
HDD carrier venting
50x3 (mm)

## Slide 6
HDDs placement
NVMe HDD with 9.0 watt
NVMe HDD with 6.3 watt

## Slide 7
2.5” NVMe HDD Temperature Profile
3x NVMe HDDs with 9.0 watt
+ 2x NVMe HDDs with 6.3 watt
can meet spec
5x NVMe HDDs with 9.0 watt
can meet spec
4x NVMe HDDs with 6.3 watt
can meet spec
X= 470 mm
NAND : 86C
NAND : 93C
* NAND spec : 85C

## Slide 8
Conclusion
Conclusion :
After changed HDDs location, x4 NVMe HDD with 9.0 watt can support to 8 pcs.
x2 NVMe HDDs are still support to 10 pcs.