## Cover
Barreleye G2-EVT-Thermal-TR-R01
Thermal Test Report
Function：Thermal
Project Name：Barreleye G2
Project Revision：EVT3
Revision：R01
Issue Date： 2017/05/15
| APPROVED |  | CHECKED | PREPARED
BY | Ken Chen |  | Ken Chen | Honda Yan
DATE |  |  |  | 2017-05-15
Foxconn CONFIDENTIAL
This document contains proprietary and confidential information jointed-develop by Foxconn. All rights and titles hereto remain with Foxconn. The recipient shall keep this document in strict confidence. The recipient shall not disclose or allow access to this document, in whole or in part, by third parties, nor use it for the benefit of the recipient or third parties. The recipient shall not change this document in form and substance by any means, including without limitation, decompile, reproduce, revise, and amend.

## History
Barreleye G2-EVT-Thermal-TR-R01
※ ※ MODIFIED HISTORY ※ ※
REV. | MODIFIED DESCRIPTION | DATE | REMARK
R01 | First Release. | 2017-05-15

## Summary
Test Configuration | [5 empty] | Reference Document
System |  |  | Barreleye G2
Power Supply
Planar Serial Number
PCB Vendor
BIOS Version
BMC FW Version
CPLD FW Version
LOM FW Version
CPU
Memory
M2010 TEST Summary
No. | Status | Items |  | Planned | Attempted | Pass | Block | Fail | Owner | Start Date | Close Date
1 |  | Thermal test. (Normal condition_6 fans) |  | 1 | 1 | 1 | #REF! | #REF! | Thermal
2 |  | Thermal test. (N+1 condition) |  | 7 | 7 | 7 | #REF! | #REF! | Thermal
3 |  | 2nd source verify (Fan, HSK) |  | 4 | 4 | 4 | #REF! | 0 | Thermal
4 |  | Wind tunnel test |  | 5 | 5 | 5 | 0 | 0 | Thermal
|  |  | Total | 17 | 17 | 17 | #REF! | #REF!
|  |  |  | Items | Attempted | Pass | Block | Fail | Process(%)
|  |  |  | 17 | 17 | 100% | #REF! | #REF! | #REF!

## Measure. Point
Barreleye G2 System setup and Measurement Points
*. SSDs location
*.Power Brick location
| * Vdn & Vddq monitor point | * Vdd & Vddq monitor point
* CPU1 (Dummy CPU) monitor point
Fan1
Fan2
Fan3
Fan4
Fan5
Fan6
CPU0
CPU1
GPU0
GPU1
Power Brick_Left
Power Brick_Right
Power Brick_MB
Vddq
Vdn
Vddq
Vdd_1
Vdd_2

## Wind tunnel
Barreleye G2 EVT System setup and Measurement Points
System Airflow rate
Sunnon | Duty cycle | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
| CFM | 21.5 | 43.2 | 65 | 87 | 109 | 131.6 | 154.2 | 177.1 | 199.5 | 205.5
Foxconn |  | 100%: 252.8
One fan failed
Nidec | Duty cycle | Fan1 fail | Fan2 fail | Fan3 fail | Fan4 fail | Fan5 fail | Fan6 fail
| CFM | 169.5 | 170.3 | 170.4 | 169.9 | 172.7 | 171.7
Foxconn | CFM | 201.4 | 205.1 | 203.3 | 202.3 | 203.5 | 205.1
System Impedance
Q | bar: 10%
| CFM | 10%: mmAq
| 9.9904 | 10%: 0.2
| 20.0448 | 10%: 0.6
| 30.0006 | 10%: 1.1
| 40.0598 | 10%: 1.7
| 50.1135 | 10%: 2.5
| 60.1177 | 10%: 3.4
| 70.1284 | 10%: 4.5
| 79.7975 | 10%: 5.7
| 89.8607 | 10%: 7
| 100.0101 | 10%: 8.5
| 110.0533 | 10%: 10
| 120.1499 | 10%: 11.7
| 130.1857 | 10%: 13.6
| 140.4166 | 10%: 15.5
| 150.4201 | 10%: 17.6
| 160.6788 | 10%: 19.7
| 171.1 | 10%: 21.7
| 182.0615 | 10%: 22.8
| 192.1175 | 10%: 24.9
| 202.9025 | 10%: 26.9
| 212.8069 | 10%: 28.9
| 221.2879 | 10%: 30.6
| 231.6377 | 10%: 33.1
| 242.0499 | 10%: 35.6
| 251.9938 | 10%: 38.4

## HDD Thermal test
G2 Thermal Verification Test Result
Objective : Check SSD' temperature at normal condition and N+1 condition.
The purpose of this test is to ensure full server functionality for the full temperature range.
Color Codes: |  | Meets Temperature Spec. |  | Slightly Exceeds Temperature Spec. |  | Exceeds Temperature Spec.
General system stress |  |  | Items |  | Case.1 | Case.2 | Case.3 | Case.4 | Case.5 | Case.6
|  |  | Configurations |  | 6 fans | 5 fans_fan6x | 6 fans | 5 fans_fan6x | 6 fans | 5 fans_fan6x
|  |  | Fan vendor |  | Sunon-15300 rpm | Sunon-15300 rpm | Sunon-15300 rpm | Sunon-15300 rpm | Foxconn-20600 rpm | Foxconn-20600 rpm
|  |  | CPU HSK vendor |  | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon
|  |  | Fan1 duty |  | 100% | 100% | 100% | 100% | 100% | 100%
|  |  | Fan2 duty |  | 100% | 100% | 100% | 100% | 100% | 100%
|  |  | Fan3 duty |  | 100% | 100% | 100% | 100% | 100% | 100%
|  |  | Fan4 duty |  | 100% | 100% | 100% | 100% | 100% | 100%
|  |  | HDD type |  | Micron SSD | Micron SSD | Samsung SSD | Samsung SSD | Samsung SSD | Samsung SSD
|  |  | Test condition |  | 35 | 35 | 35 | 35C | 35 | 35C
CH | Location |  | Temp Spec
101 | Ambient_1 |  | Ta | NA | 35.0392 | 34.9598 | 35.0061 | 34.9771 | 35.0067 | 34.9502
102 | Ambient_2 |  | Ta | NA | 35.1503 | 35.1141 | 35.3122 | 35.1275 | 35.2345 | 35.1421
103 | HDD11 |  | Tc | 70 | 40.4729 | 41.2086 | 40.0623 | 40.8255 | 39.1374 | 39.9501
104 | HDD12 |  | Tc | 70 | 40.8271 | 41.7121 | 40.3522 | 41.2125 | 39.3962 | 40.2705
105 | HDD13 |  | Tc | 70 | 40.6191 | 41.4802 | 40.3604 | 41.2405 | 39.4041 | 40.3001
106 | HDD14 |  | Tc | 70 | 40.7411 | 41.6487 | 40.3001 | 41.166 | 39.3624 | 40.2388
107 | HDD15 |  | Tc | 70 | 40.324 | 41.0767 | 40.1532 | 40.8578 | 39.3564 | 40.0574
108 | HDD16 |  | Tc | 70 | 41.9874 | 42.8768 | 41.1141 | 42.0236 | 40.0757 | 41.0282
109 | HDD17 |  | Tc | 70 | 42.5116 | 43.5191 | 41.7655 | 42.7974 | 40.6595 | 41.692
110 | HDD18 |  | Tc | 70 | 42.4349 | 43.5269 | 41.6913 | 42.761 | 40.6263 | 41.6338
111 | HDD19 |  | Tc | 70 | 42.0534 | 43.1074 | 41.6886 | 42.6718 | 40.6245 | 41.6339
112 | HDD20 |  | Tc | 70 | 41.1576 | 42.0463 | 41.1069 | 41.9256 | 40.1762 | 41.0188
113 | HDD21 |  | Tc | 70 | 41.7166 | 42.5542 | 41.0936 | 42.0115 | 40.0405 | 40.9069
114 | HDD22 |  | Tc | 70 | 42.1927 | 43.1223 | 41.9775 | 43.0331 | 40.8298 | 41.7894
115 | HDD23 |  | Tc | 70 | 42.2713 | 43.2598 | 41.9543 | 42.9946 | 40.8211 | 41.8244
116 | HDD24 |  | Tc | 70 | 41.3985 | 42.3771 | 40.9088 | 41.897 | 39.9396 | 40.8828
117 | Power Brick_MB |  | Tc | 125 | 49.378 | 51.0066 | 49.3966 | 50.9862 | 47.8918 | 49.4057
118 | Power Brick_Left |  | Tc | 125 | 57.6307 | 58.3136 | 57.7236 | 58.3386 | 60.2117 | 59.1438
119 | Power Brick_Right |  | Tc | 125 | 57.5281 | 58.3339 | 57.651 | 58.4373 | 55.9777 | 56.6964
Conclusion : 1. Micron and Samsung SSD can meet thermal spec at normal condition and N+1 condition (fan6 failed).

## CPU Thermal test
Barreleye G2 Thermal Verification Test Result
Objective : Check components' temperature at normal condition and N+1 condition.
The purpose of this test is to ensure full server functionality for the full temperature range.
Color Codes: |  | Meets Temperature Spec. |  | Slightly Exceeds Temperature Spec. |  | Exceeds Temperature Spec.
General system stress |  |  | Items |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 5 | 7 | 7
|  |  | Configurations |  | Normal condition | N+1 | N+1 | N+1 | N+1 | N+1 | N+1 | Normal condition | N+1_fan4 failed | N+1_fan4 failed
|  |  | Fan vendor |  | Sunon-15300 rpm | Sunon-15300 rpm | Sunon-15300 rpm | Sunon-15300 rpm | Sunon-15300 rpm | Sunon-15300 rpm | Sunon-15300 rpm | Foxconn-20600 rpm | Foxconn-20600 rpm | Foxconn-20600 rpm
|  |  | CPU HSK vendor |  | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon | Forcecon
|  |  | Fan1 duty |  | 100% | Fan1 failed | Fan2 failed | Fan3 failed | Fan4 failed | Fan5 failed | Fan6 failed | 100% | Fan1 failed | Fan4 failed
|  |  | Test condition |  | 35C | 35C | 35C | 35C | 35C | 35C | 35C | 35C | 35C | 35C
CH | Location |  | Temp Spec
101 | Ambient_1 |  | Ta | Ref | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
102 | Ambient_2 |  | Ta | Ref | 35.4323 | 35.046 | 35.1298 | 34.982 | 35.056 | 35.0988 | 35.3305 | 35.396 | 35.2417 | 35.519
103 | HDD11 |  | Tc | 70 | 39.8277 | 40.5806 | 40.6113 | 40.6521 | 40.515 | 40.8689 | 40.6176 | 39.263 | 39.9521 | 39.9756
104 | HDD12 |  | Ta | 70 | 40.1046 | 40.9179 | 40.9729 | 41.0313 | 40.8306 | 41.2403 | 40.989 | 39.5507 | 40.2551 | 40.2211
105 | HDD13 |  | Ta | 70 | 40.1262 | 40.9023 | 40.98 | 41.055 | 40.7616 | 41.2446 | 40.9909 | 39.5731 | 40.2752 | 40.204
106 | HDD14 |  | Tc | 70 | 40.0846 | 40.8191 | 40.9218 | 40.9979 | 40.6304 | 41.1777 | 40.905 | 39.5427 | 40.2256 | 40.1344
107 | HDD15 |  | Ta | 70 | 39.9686 | 40.5487 | 40.6664 | 40.7406 | 40.3147 | 40.9076 | 40.5912 | 39.562 | 40.0783 | 39.9861
108 | HDD16 |  | Ta | 70 | 40.868 | 41.737 | 41.8198 | 41.8572 | 41.6723 | 42.0889 | 41.7207 | 40.2869 | 41.0685 | 41.0908
109 | HDD17 |  | Ta | 70 | 41.5247 | 42.4951 | 42.5724 | 42.6331 | 42.3895 | 42.8644 | 42.501 | 40.8694 | 41.7252 | 41.7038
110 | HDD18 |  | Tc | 70 | 41.4556 | 42.4076 | 42.5023 | 42.5721 | 42.2623 | 42.7969 | 42.4374 | 40.8352 | 41.6622 | 41.5985
111 | HDD19 |  | Tc | 70 | 41.4804 | 42.3299 | 42.4418 | 42.5193 | 42.1619 | 42.7587 | 42.3958 | 40.8509 | 41.6893 | 41.5951
112 | HDD20 |  | Tc | 70 | 40.9159 | 41.5998 | 41.727 | 41.8029 | 41.3955 | 42.0351 | 41.6736 | 40.4268 | 41.0962 | 40.9977
113 | HDD21 |  | Tc | 70 | 40.8471 | 41.9014 | 41.9952 | 41.9919 | 41.6766 | 42.085 | 41.6065 | 40.2261 | 40.9036 | 41.0582
114 | HDD22 |  | Tc | 70 | 41.7313 | 42.9283 | 42.9914 | 43.0248 | 42.6521 | 43.1111 | 42.6458 | 41.0232 | 41.8234 | 41.9065
115 | HDD23 |  | Tc | 70 | 41.7682 | 42.8451 | 42.9244 | 42.9804 | 42.5858 | 43.1336 | 42.7171 | 41.0832 | 41.9089 | 41.9133
116 | HDD24 |  | Tc | 70 | 40.8491 | 41.616 | 41.7343 | 41.8067 | 41.4835 | 42.1066 | 41.7622 | 40.3186 | 41.0768 | 40.9451
117 | Power Brick_MB |  | Tc | 125 | 49.2628 | 50.7604 | 50.8765 | 50.8426 | 50.5114 | 50.7437 | 50.7103 | 48.1658 | 49.5814 | 49.6059
118 | Power Brick_Left |  | Tc | 125 | 59.2257 | 52.6186 | 60.2279 | 63.0551 | 61.5836 | 61.7134 | 61.3343 | 63.0816 | 62.9492 | 63.9976
119 | Power Brick_Right |  | Tc | 125 | 60.0019 | 56.772 | 56.7827 | 60.7312 | 59.3781 | 59.4643 | 59.2233 | 59.0309 | 57.9012 | 58.5997
203 | CPU0 inlet_1 |  | Ta | Ref | 36.0681 | 35.7982 | 35.8825 | 35.6687 | 35.7447 | 35.7967 | 35.9366 | 36.067 | 35.9666 | 36.2559
203 | CPU0 inlet_2 |  | Ta | Ref | 37.9124 | 38.2908 | 38.4053 | 38.2694 | 37.9219 | 38.0471 | 38.1194 | 37.8012 | 37.9328 | 38.1769
22 | CPU0 |  | Tc | 70 | 48.0887 | 49.3096 | 49.2983 | 49.1248 | 49.1378 | 49.2199 | 49.2429 | 47.4413 | 48.3088 | 48.6106
23 | CPU1 inlet_1 |  | Ta | Ref | 35.8022 | 35.6871 | 35.7087 | 35.5841 | 35.7306 | 35.6644 | 35.7352 | 35.7837 | 35.7871 | 35.9588
203 | CPU1 inlet_2 |  | Ta | Ref | 37.1746 | 37.4495 | 37.4659 | 37.2983 | 37.5317 | 37.45 | 37.4988 | 36.8699 | 37.1768 | 37.5416
203 | CPU1 |  | Tc | 70 | 65.3154 | 67.6239 | 67.5913 | 67.4375 | 67.5636 | 67.3902 | 67.3387 | 63.1061 | 65.1356 | 65.4555
22 | DIMM2 |  | Tc | 85 | 38.3792 | 38.7792 | 38.8825 | 38.7631 | 38.6238 | 38.8961 | 38.8037 | 38.1427 | 38.4745 | 38.6359
23 | DIMM5 |  | Tc | 85 | 41.3389 | 42.2716 | 42.3007 | 42.1543 | 42.0733 | 42.1715 | 42.0921 | 40.652 | 41.3422 | 41.6017
22 | DIMM10 |  | Tc | 85 | 39.6845 | 40.3898 | 40.4693 | 40.387 | 40.4482 | 40.5401 | 40.4856 | 39.1586 | 39.8413 | 39.9944
23 | DIMM13 |  | Tc | 85 | 40.2198 | 41.0066 | 41.0456 | 40.9984 | 41.0019 | 41.0756 | 40.9259 | 39.7115 | 40.2924 | 40.4466
22 | CX-4 25G |  | Tc | 100 | 37.6236 | 37.7418 | 37.8315 | 37.7261 | 37.7933 | 37.7984 | 37.7519 | 37.6615 | 37.6582 | 37.6844
203 | CPU0 VDDQ |  | Ta | 100 | 44.0219 | 44.9394 | 44.9663 | 44.8312 | 44.8002 | 44.9783 | 45.0597 | 43.5204 | 44.1931 | 44.4306
22 | CPU0 VDD_2 |  | Tc | 100 | 43.8079 | 44.7609 | 44.7724 | 44.6337 | 44.6079 | 44.772 | 44.813 | 43.2771 | 43.9516 | 44.2048
23 | CPU0 VDD_1 |  | Ta | 100 | 43.6752 | 44.6602 | 44.6577 | 44.5201 | 44.5081 | 44.6469 | 44.6672 | 43.1356 | 43.8282 | 44.0858
203 | CPU0 VDDQ |  | Ta | 100 | 39.2913 | 39.5561 | 39.5584 | 39.4511 | 39.333 | 39.5584 | 39.555 | 39.2285 | 39.3256 | 39.4771
203 | CPU0 VDN |  | Tc | 100 | 39.0985 | 39.3385 | 39.3298 | 39.2159 | 39.0852 | 39.3393 | 39.2925 | 39.0545 | 39.1301 | 39.2754
22 | CPU1 VDN |  | Tc | 100 | 39.9916 | 40.3806 | 40.4555 | 40.3781 | 40.3823 | 40.4114 | 40.3567 | 39.9252 | 40.0612 | 40.1733
23 | CPU1 VDDQ |  | Tc | 100 | 39.6279 | 40.004 | 40.0887 | 40.009 | 40.004 | 40.0521 | 39.9701 | 39.5253 | 39.6622 | 39.7812
22 | CPU1 VDD_1 |  | Tc | 100 | 44.9453 | 46.3294 | 46.4103 | 46.3408 | 46.4439 | 46.4512 | 46.3761 | 44.0021 | 45.1149 | 45.3526
23 | CPU1 VDD_2 |  | Tc | 100 | 45.0967 | 46.3661 | 46.4362 | 46.3776 | 46.4535 | 46.493 | 46.3722 | 44.2173 | 45.2487 | 45.4608
22 | CPU1 VDDQ |  | Tc | 100 | 45.3941 | 46.7669 | 46.8449 | 46.7809 | 46.8559 | 46.8856 | 46.7795 | 44.4367 | 45.5589 | 45.7861
Conclusion : 1. All components can meet thermal spec at normal condition and N+1 condition, but GPUs can't stress at EVT stage. It has risk to impact system thermal solutions. Need to double check system thermal when GPUs can stress under OS. 2. DD1 CPU can't full stress when run HTX tools. And CPUs' t-junction temperature and power also can't read. It will also has risk to impact CPU heat sink design.